## PUBLIC GEN DATA 2017-18
Company | Jurisdiction | SEM-ID | PLEXOS-ID | Name | Node | Voltage(kV) | YearOf Connection | ChangeDateforNewUnitCharacteristics | StartFuel1 | Percent1 | StartFuel2 | Percent2 | Type | MinStableCapacity(MW) | MEC(MW) | SummerMEC(MW) | NoLoadHeatRequirement(GJ/ hr) | CapacityPoint1(MW) | Capacitypoint2(MW) | Capacitypoint3(MW) | Capacitypoint4(MW) | Capacitypoint5(MW) | HeatRateInc1(GJ/ MWh) | HeatRateInc2(GJ/ MWh) | HeatRateInc3(GJ/ MWh) | HeatRateInc4(GJ/ MWh) | HeatRateInc5(GJ/ MWh) | ForcedOutageRate(%) | MeanTimetoRepair(hrs) | RampRateUp(MW/ min) | RampRateDown(MW/ min) | MinUpTime(hrs) | MinDownTime(hrs) | StartupEnergy(GJ)Hot | StartupEnergy(GJ)Warm | StartupEnergy(GJ)Cold | HottoWarmboundary(hrs) | WarmtoColdboundary(hrs) | Notes
ESB | ROI | GU_400180 | AD1 | Aghada 1 | Aghada | 220 | 2000 |  | Gas | 100% |  |  | Gas | 36 | 258 |  | 187.432 | 120 | 190 | 258 |  |  | 8.013 | 8.674 | 8.748 |  |  | 0.062 | 480 | 3.87 | 3.86 | 4 | 3.5 | 1273 | 2185 | 4302 | 5 | 67
ESB | ROI | GU_400850 | ADC | Aghada CCGT | Longpoint | 220 | 2010 |  | Gas | 100% |  |  | Gas | 216 | 444 | 449 | 589.4 | 220 | 430 | 440 | 444 |  | 4.24 | 5.364 | 5.525 | 5.525 |  | 0.062 | 192 | 8.83 | 12.38 | 4 | 1 | 1200 | 1800 | 2400 | 12 | 60
ESB | ROI | GU_400181 | AT1 | Aghada CT 1 | Aghada | 220 | 2000 |  | Gas | 100% |  |  | Gas | 15 | 90 |  | 281 | 40 | 90 |  |  |  | 7.712 | 9.569 |  |  |  | 0.062 | 174 | 5 | 5 | 4 | 1 | 63
ESB | ROI | GU_400182 | AT2 | Aghada CT 2 | Aghada | 220 | 2000 |  | Gas | 100% |  |  | Gas | 15 | 90 |  | 281 | 40 | 90 |  |  |  | 7.712 | 9.569 |  |  |  | 0.062 | 174 | 5 | 5 | 4 | 1 | 63
ESB | ROI | GU_400183 | AT4 | Aghada CT 4 | Aghada | 220 | 2000 |  | Gas | 100% |  |  | Gas | 15 | 90 |  | 281 | 40 | 90 |  |  |  | 7.712 | 9.569 |  |  |  | 0.062 | 174 | 5 | 5 | 4 | 1 | 63
ESB | ROI | GU_400200 | AA1 | Ardnacrusha 1 | Ardnacrusha | 110 | 2000 |  | Water | 100% |  |  | Water |  | 21 | [12 empty] | 0.045 | 86 | 0.42 | 0.42
ESB | ROI | GU_400201 | AA2 | Ardnacrusha 2 | Ardnacrusha | 110 | 2000 |  | Water | 100% |  |  | Water |  | 22 | [12 empty] | 0.045 | 86 | 0.47 | 0.47
ESB | ROI | GU_400202 | AA3 | Ardnacrusha 3 | Ardnacrusha | 110 | 2000 |  | Water | 100% |  |  | Water |  | 19 | [12 empty] | 0.045 | 86 | 0.33 | 0.33
ESB | ROI | GU_400203 | AA4 | Ardnacrusha 4 | Ardnacrusha | 110 | 2000 |  | Water | 100% |  |  | Water |  | 24 | [12 empty] | 0.045 | 82 | 0.55 | 0.55
BnM | ROI | GU_401010 | ED3 | Cushaling | Cushaling | 110 | 2010 |  | Gasoil | 100% |  |  | Gasoil | 20 | 58 |  | 85 | 58 |  |  |  |  | 9.5 |  |  |  |  | 0.024 | 24 | 5 | 5 |  | 0.5 | 22
BnM | ROI | GU_401011 | ED5 | Cushaling | Cushaling | 110 | 2010 |  | Gasoil | 100% |  |  | Gasoil | 20 | 58 |  | 85 | 58 |  |  |  |  | 9.5 |  |  |  |  | 0.024 | 24 | 5 | 5 |  | 0.5 | 22
ESB | ROI | GU_400500 | DB1 | Dublin Bay CCGT | Irishtown | 220 | 2002 |  | Gas | 100% |  |  | Gas | 203 | 423 | 415 | 594.7 | 203 | 405 | 415 | 416 |  | 4.018 | 5.679 | 5.679 | 5.679 |  | 0.062 | 176 | 10 | 9 | 4 | 1 | 2600 | 2604 | 7700 | 12 | 60
Covanta | ROI |  | Dublin | Dublin Waste to Energy | Poolbeg | 220 | 2017 | 2017-10-01 | Gasoil | 100% |  |  | Waste | 21.35 | 68.197 | 67.564 | [11 empty] | 0.067 | 36 | 0.915 | 0.915 |  |  | 1323.7 | 1558.55 |  | 24 | >24
BnM | ROI | GU_401860 | ED1 | Edenderry | Cushaling | 110 | 2000 |  | Gasoil | 100% |  |  | Peat | 41 | 117.6 |  | 497.6 | 88 | 112 | 118 |  |  | 3.933 | 8.95 | 8.95 |  |  | 0.079 | 72 | 1.76 | 1.76 | 4 | 0.5 | 436 | 1084 | 2308 | 12 | 48
ESB | ROI | GU_400210 | ER1 | Erne 1 | Cathaleen's Fall | 110 | 2000 |  | Water | 100% |  |  | Water |  | 10 | [12 empty] | 0.045 | 86 | 5 | 10
ESB | ROI | GU_400211 | ER2 | Erne 2 | Cathaleen's Fall | 110 | 2000 |  | Water | 100% |  |  | Water |  | 10 | [12 empty] | 0.045 | 86 | 5 | 10
ESB | ROI | GU_400220 | ER3 | Erne 3 | Cliff | 110 | 2000 |  | Water | 100% |  |  | Water |  | 22.5 | [12 empty] | 0.045 | 83 | 10 | 22.5
ESB | ROI | GU_400221 | ER4 | Erne 4 | Cliff | 110 | 2000 |  | Water | 100% |  |  | Water |  | 22.5 | [12 empty] | 0.045 | 86 | 10 | 22.5
SSE | ROI | GU_400762 | GI CCGT | Great Island CCGT | Great Island | 220 | 2014 |  | Gas | 100% |  |  | Gas | 165 | 464 | 458.5 | 605 | 203 | 320 | 464 |  |  | 4.0891 | 5.4069 | 5.6228 |  |  | 0.062 | 55 | 17.17 | 18.5 | 4 | 4 | 1100 | 1700 | 3300 | 12 | 60
Viridian | ROI | GU_400480 | HNC | Huntstown | Huntstown | 220 | 2002 |  | Gas | 100% |  |  | Gas | 120 | 343 | 332.71 | 541.204 | 120 | 171 | 230 | 250 | 352 | 4.528 | 4.53 | 5.237 | 5.247 | 6.039 | 0.062 | 55 | 7 | 7 | 4 | 4 | 834.687 | 2803.196 | 4771.682 | 12 | 60
Viridian | ROI | GU_400540 | HN2 | Huntstown Phase II | Corduff | 220 | 2007 |  | Gas | 100% |  |  | Gas | 121 | 404 | 391.88 | 603.6 | 121 | 150 | 170 | 230 | 412 | 4.1271 | 4.129 | 4.7549 | 5.4288 | 5.7167 | 0.062 | 55 | 20 | 20 | 4 | 4 | 318.454 | 531.129 | 644.171 | 12 | 60
ESB | ROI | GU_400280 | LE1 | Lee 1 | Inniscarra | 110 | 2000 |  | Water | 100% |  |  | Water |  | 15 | [12 empty] | 0.045 | 123 | 0.2 | 15
ESB | ROI | GU_400281 | LE2 | Lee 2 | Inniscarra | 110 | 2000 |  | Water | 100% |  |  | Water |  | 4 | [12 empty] | 0.045 | 123 | 0.2 | 4
ESB | ROI | GU_400290 | LE3 | Lee 3 | Carrigadrohid | 110 | 2000 |  | Water | 100% |  |  | Water |  | 8 | [12 empty] | 0.045 | 83 | 1.5 | 8
ESB | ROI | GU_400250 | LI1 | Liffey 1 | Pollaphuca | 110 | 2000 |  | Water | 100% |  |  | Water |  | 15 | [12 empty] | 0.045 | 130 | 5 | 10
ESB | ROI | GU_400251 | LI2 | Liffey 2 | Pollaphuca | 110 | 2000 |  | Water | 100% |  |  | Water |  | 15 | [12 empty] | 0.045 | 130 | 5 | 10
ESB | ROI | GU_400252 | LI4 | Liffey 4 | Pollaphuca | 110 | 2000 |  | Water | 100% |  |  | Water |  | 4 | [12 empty] | 0.045 | 90 | 2 | 2
ESB | ROI | GU_400260 | LI5 | Liffey 5 | Pollaphuca | 110 | 2000 |  | Water | 100% |  |  | Water |  | 4 | [12 empty] | 0.045 | 130 | 0.03 | 2
ESB | ROI | GU_400240 | LR4 | Lough Ree | Lanesboro | 110 | 2000 |  | Peat | 100% |  |  | Peat | 91 | 93 |  | 86.8 | 91 | 93 |  |  |  | 8.811 | 8.811 |  |  |  | 0.079 | 339 | 0.5 | 0.5 | 4 | 4 | 300 | 400 | 500 | 12 | 48
ESB | ROI | GU_400300 | MRC | Marina | Marina | 110 | 2000 |  | Gas | 100% |  |  | Gas | 45 | 95 |  | 258.4 | 47 | 81 | 95 |  |  | 8.644 | 9.462 | 11.393 |  |  | 0.062 | 72 | 5 | 5 | 1 | 0.5 | 50
Indaver | ROI | GU_401230 | IW1 | Meath waste to energy | Drybridge | 110 | 2011 | [5 empty] | Waste | 1 | 17 | [12 empty] | 0.067 | 2.3 | 0.36 | 0.65
ESB | ROI | GU_400270 | MP1 | Moneypoint 1 | Moneypoint | 380 | 2000 |  | Coal | 68% | Gasoil | 32% | Coal | 99 | 285 |  | 189 | 195 | 280 | 285 |  |  | 9.15 | 9.242 | 13.696 |  |  | 0.091 | 284 | 1.63 | 4.54 | 6 | 5 | 4360 | 6920 | 14620 | 12 | 60
ESB | ROI | GU_400271 | MP2 | Moneypoint 2 | Moneypoint | 380 | 2000 |  | Coal | 68% | Gasoil | 32% | Coal | 99 | 285 |  | 189 | 195 | 280 | 285 |  |  | 9.15 | 9.242 | 13.696 |  |  | 0.091 | 283 | 1.63 | 4.49 | 6 | 5 | 4360 | 6920 | 14620 | 12 | 60
ESB | ROI | GU_400272 | MP3 | Moneypoint 3 | Moneypoint | 380 | 2000 |  | Coal | 68% | Gasoil | 32% | Coal | 99 | 285 |  | 189 | 195 | 280 | 285 |  |  | 9.15 | 9.242 | 13.696 |  |  | 0.091 | 284 | 1.63 | 4.54 | 6 | 5 | 4360 | 6920 | 14620 | 12 | 60
ESB | ROI | GU_400311 | NW5 | North Wall 5 | North Wall | 220 | 2000 |  | Gas | 100% |  |  | Gas | 4.01 | 109 |  | 323.3 | 50 | 109 |  |  |  | 8.887 | 8.887 |  |  |  | 0.062 | 328 | 8 | 8 | 4 | 0.5 | 50
ESB | ROI | GU_400324 | PBA | Poolbeg C_A | Shellybanks | 220 | 2000 |  | Gas | 100% |  |  | Gas | 120 | 256 |  | 352.9 | 145 | 240 | 255 |  |  | 5.435 | 6.057 | 7.007 |  |  | 0.062 | 154 | 11 | 11 | 4 | 4 | 750 | 900 | 1400 | 8 | 52
ESB | ROI | GU_400325 | PBB | Poolbeg C_B | Shellybanks | 220 | 2000 |  | Gas | 100% |  |  | Gas | 120 | 256 |  | 352.9 | 145 | 240 | 255 |  |  | 5.435 | 6.057 | 7.007 |  |  | 0.062 | 154 | 11 | 11 | 4 | 4 | 750 | 900 | 1400 | 8 | 52
SSE | ROI | GU_400330 | RH1 | Rhode 1 | Derryiron | 110 | 2004 |  | Gasoil | 100% |  |  | Gasoil | 5 | 52 |  | 85.01 | 12 | 52 |  |  |  | 9.8226 | 9.8226 |  |  |  | 0.024 | 50 | 10 | 10 |  | 0.75 | 24
SSE | ROI | GU_400331 | RH2 | Rhode 2 | Derryiron | 110 | 2004 |  | Gasoil | 100% |  |  | Gasoil | 5 | 52 |  | 85.01 | 12 | 52 |  |  |  | 9.8226 | 9.8226 |  |  |  | 0.024 | 50 | 10 | 10 |  | 0.75 | 24
Aughinish | ROI | GU_400120 | SK3 | Sealrock 3 (Aughinish CHP) | Aughinish | 110 | 2005 |  | Gas | 100% |  |  | Gas | 40 | 83 |  | 100 | 40 | 83 |  |  |  | 5 | 5 |  |  |  | 0.062 | 44 | 6 | 6 | 4 | 4 | 800 | 1000 | 1200 | 12 | 48
Aughinish | ROI | GU_400121 | SK4 | Sealrock 4 (Aughinish CHP) | Aughinish | 110 | 2005 |  | Gas | 100% |  |  | Gas | 40 | 83 |  | 100 | 40 | 83 |  |  |  | 5 | 5 |  |  |  | 0.062 | 44 | 6 | 6 | 4 | 4 | 800 | 1000 | 1200 | 12 | 48
SSE | ROI | GU_400340 | TB1 | Tarbert Unit 1 | Tarbert | 110 | 2000 |  | Oil | 61% | Gasoil | 39% | Oil | 18 | 54 |  | 44.66 | 20 | 46 | 54 |  |  | 11.63 | 11.63 | 11.75 |  |  | 0.02 | 50 | 1 | 1 | 2 | 2 | 217.5 | 449 | 562 | 12 | 48
SSE | ROI | GU_400341 | TB2 | Tarbert Unit 2 | Tarbert | 110 | 2000 |  | Oil | 61% | Gasoil | 39% | Oil | 18 | 54 |  | 44.66 | 20 | 46 | 54 |  |  | 11.63 | 11.63 | 11.75 |  |  | 0.02 | 50 | 1 | 1 | 2 | 2 | 217.5 | 449 | 562 | 12 | 48
SSE | ROI | GU_400342 | TB3 | Tarbert Unit 3 | Tarbert | 220 | 2000 |  | Oil | 70% | Gasoil | 30% | Oil | 34.85 | 243 |  | 247.61 | 34.85 | 100 | 180 | 240 |  | 8.0698 | 8.0698 | 9.063 | 9.153 |  | 0.02 | 50 | 2 | 2.2 | 4 | 4 | 1072 | 1934 | 3180 | 14 | 106
SSE | ROI | GU_400343 | TB4 | Tarbert Unit 4 | Tarbert | 220 | 2000 |  | Oil | 70% | Gasoil | 30% | Oil | 34.85 | 243 |  | 247.61 | 34.85 | 100 | 180 | 240 |  | 8.4 | 8.4 | 9.428 | 9.64 |  | 0.02 | 50 | 2 | 2.2 | 4 | 4 | 1072 | 1934 | 3180 | 14 | 106
SSE | ROI | GU_400350 | TP1 | Tawnaghmore 1 | Tawnaghmore | 110 | 2006 |  | Gasoil | 100% |  |  | Gasoil | 5 | 52 |  | 86.62 | 12 | 52 |  |  |  | 9.5867 | 9.5867 |  |  |  | 0.024 | 50 | 10 | 10 |  | 0.75 | 24
SSE | ROI | GU_400351 | TP3 | Tawnaghmore 3 | Tawnaghmore | 110 | 2008 |  | Gasoil | 100% |  |  | Gasoil | 5 | 52 |  | 86.62 | 12 | 52 |  |  |  | 9.5867 | 9.5867 |  |  |  | 0.024 | 50 | 10 | 10 |  | 0.75 | 24
ESB | ROI | GU_400360 | TH1 | Turlough Hill 1 | Turlough Hill | 220 | 2000 |  | Water | 100% |  |  | Water |  | 73 | [12 empty] | 0.06 | 123
ESB | ROI | GU_400361 | TH2 | Turlough Hill 2 | Turlough Hill | 220 | 2000 |  | Water | 100% |  |  | Water |  | 73 | [12 empty] | 0.06 | 123
ESB | ROI | GU_400362 | TH3 | Turlough Hill 3 | Turlough Hill | 220 | 2000 |  | Water | 100% |  |  | Water |  | 73 | [12 empty] | 0.06 | 123
ESB | ROI | GU_400363 | TH4 | Turlough Hill 4 | Turlough Hill | 220 | 2000 |  | Water | 100% |  |  | Water |  | 73 | [12 empty] | 0.06 | 123
Tynagh | ROI | GU_400530 | TY | Tynagh | Tynagh | 220 | 2006 |  | Gas | 100% |  |  | Gas | 194 | 404 | 377.7 | 594 | 200 | 250 | 330 | 404 | 405 | 4.7737 | 4.9603 | 5.353 | 6.2127 | 26.856 | 0.062 | 32.1 | 15 | 12.5 | 4 | 4 | 1200 | 2000 | 3000 | 12 | 48
ESB | ROI | GU_400370 | WO4 | West Offaly | Shannonbridge | 110 | 2005 |  | Peat | 100% |  |  | Peat | 137 | 140 |  | 120.5 | 137 | 140 |  |  |  | 8.659 | 8.659 |  |  |  | 0.079 | 339 | 0.7 | 0.7 | 4 | 4 | 450 | 600 | 750 | 12 | 60
BGE | ROI | GU_400930 | WG | Whitegate | Glanagow | 220 | 2010 |  | Gas | 100% |  |  | Gas | 180 | 445 | 432 | 666.68 | 185 | 399 | 460 |  |  | 3.91 | 5.265 | 5.265 |  |  | 0.062 | 32.1 | 20.6 | 26.8 | 4 | 4 | 222.604 | 329.866 | 437.127 | 12 | 60
POWERNI | NI | GU_500140 | B10 | Ballylumford CCGT Unit 10 |  |  |  |  | Gas | 100% |  |  | Gas | 63 | 101 | 98.9 | 98.15 | 88 | 101 |  |  |  | 6.003 | 6.003 |  |  |  | 0.062 | 72 | 1.09 | 4 | 0.02 | 0.25 | 135 | 225 | 405 | 8 | 40
POWERNI | NI | GU_500130 | B31 | Ballylumford CCGT Unit 31 |  |  |  |  | Gas | 100% |  |  | Gas | 113 | 247 | 244.1 | 390 | 113 | 247 |  |  |  | 5.715 | 5.715 |  |  |  | 0.062 | 72 | 11 | 11 | 0.02 | 0.25 | 639 | 1134 | 2025 | 8 | 40
POWERNI | NI | GU_500131 | B32 | Ballylumford CCGT Unit 32 |  |  |  |  | Gas | 100% |  |  | Gas | 113 | 247 | 244.1 | 390 | 113 | 247 |  |  |  | 5.715 | 5.715 |  |  |  | 0.062 | 72 | 11 | 11 | 0.02 | 0.25 | 639 | 1134 | 2025 | 8 | 40
AES | NI | GU_500100 | B4 | Ballylumford Unit 4 |  |  |  |  | Gas | 100% |  |  | Gas | 54 | 144 |  | 212.99 | 54 | 143.5 |  |  |  | 11.453 | 11.453 |  |  |  | 0.062 | 36 | 1.98 | 9.67 | 2 | 1 | 764.5784 | 1378.4077 | 1917.3136 | 10 | 26
AES | NI | GU_500110 | B5 | Ballylumford Unit 5 |  |  |  |  | Gas | 100% |  |  | Gas | 54 | 147 |  | 210.01 | 54 | 146.5 |  |  |  | 11.105 | 11.105 |  |  |  | 0.062 | 36 | 1.98 | 9.67 | 2 | 1 | 764.5784 | 1378.4077 | 1917.3136 | 10 | 26
Full Circle Generation | NI |  | Belfast Waste | Belfast Waste to Energy |  |  |  | 2018-01-01 | Oil | 100% |  |  | Waste | 10 | 14.8 | [12 empty] | 0.067 | 24 | 0.04 | 0.04 | 4 | 0.5 | 2000 | 4000 | 6000 | 2 | 4
AES | NI | GU_500150 | BGT1 | Ballylumford GT1 |  |  |  |  | Gasoil | 100% |  |  | Gasoil | 8 | 58 |  | 180 | 8 | 53 | 58 |  |  | 11.05 | 11.05 | 11.05 |  |  | 0.024 | 72 | 5 | 6.43 | 0.02 | 0.25 | 8
AES | NI | GU_500160 | BGT2 | Ballylumford GT2 |  |  |  |  | Gasoil | 100% |  |  | Gasoil | 8 | 58 |  | 180 | 8 | 53 | 58 |  |  | 11.05 | 11.05 | 11.05 |  |  | 0.024 | 72 | 5 | 6.43 | 0.02 | 0.25 | 8
ESB | NI | GU_500041 | CGT8 | Coolkeeragh OCGT |  |  |  |  | Gasoil | 100% |  |  | Gasoil | 8 | 53 |  | 180 | 53 |  |  |  |  | 11.05 |  |  |  |  | 0.024 | 469 | 50 | 50 | 0.02 | 0.25 | 8
Contour | NI | GU_500904 | Contour AGU | Contour Global Agg Unit |  |  |  |  | Gas | 100% |  |  | Gas | 6 | 12.084 |  | 15.408 | 9 | 12 |  |  |  | 7.632 | 8.316 |  |  |  | 0.062 | 48 | 4.032 | 4.032 | 0.5 | 0.5 | 0.62
ESB | NI | GU_500040 | CPS CCGT | Coolkeeragh CCGT |  |  |  |  | Gas | 100% |  |  | Gas | 260 | 412 |  | 633.76 | 260 | 328 | 372 | 404 | 412 | 4.384 | 5.341 | 5.573 | 5.603 | 5.603 | 0.062 | 176 | 15 | 8.35 | 4 | 4 | 1088 | 3046 | 5257 | 12 | 38
iPower | NI | GU_501130 | iPower AGU | iPower AGU |  |  |  |  | Gasoil | 100% |  |  | Gasoil |  | 72 |  | 27 |  | 72 |  |  |  | 12.8 | 12.8 |  |  |  | 0.024 | 24 | 8 | 8 | 0.5 | 0.5 | 70
AES | NI | GU_500060 | K1 Coal 220 | Kilroot Unit 1 FGD |  |  |  |  | Oil | 80% | Coal | 20% | Coal | 93 | 255 |  | 393.605 | 93 | 174.8 | 199 | 237.6 |  | 8.97 | 8.97 | 8.97 | 51.28 |  | 0.091 | 24 | 5.79 | 5.79 | 4 | 0.5 | 2947 | 5134 | 6827 | 10 | 55
AES | NI | GU_500070 | K2 Coal 220 | Kilroot Unit 2 FGD |  |  |  |  | Oil | 80% | Coal | 20% | Coal | 93 | 258 |  | 393.605 | 93 | 174.8 | 199 | 237.6 |  | 8.97 | 8.97 | 8.97 | 51.28 |  | 0.091 | 24 | 5.79 | 5.79 | 4 | 0.5 | 2947 | 5134 | 6827 | 10 | 55
AES | NI | GU_500080 | KGT1 | Kilroot GT1 |  |  |  |  | Gasoil | 100% |  |  | Gasoil | 5 | 29 |  | 103 | 5 | 23.6 | 29.2 |  |  | 11.05 | 11.05 | 11.05 |  |  | 0.024 | 24 | 2.67 | 2.67 | 0.02 | 0.25 | 8
AES | NI | GU_500090 | KGT2 | Kilroot GT2 |  |  |  |  | Gasoil | 100% |  |  | Gasoil | 5 | 29 |  | 103 | 5 | 23.6 | 29.2 |  |  | 11.05 | 11.05 | 11.05 |  |  | 0.024 | 24 | 2.67 | 2.67 | 0.02 | 0.25 | 8
AES | NI | GU_500820 | KGT3 | Kilroot GT3 |  |  |  |  | Gasoil | 100% |  |  | Gasoil | 12.8194 | 42 |  | 115.3926 | 12.8194 | 41.6075 |  |  |  | 9.2356 | 9.2356 |  |  |  | 0.024 | 24 | 10 | 10 | 0.62 | 0.38 | 10
AES | NI | GU_500821 | KGT4 | Kilroot GT4 |  |  |  |  | Gasoil | 100% |  |  | Gasoil | 12.8194 | 42 |  | 115.3926 | 12.8194 | 41.6075 |  |  |  | 9.2356 | 9.2356 |  |  |  | 0.024 | 24 | 10 | 10 | 0.62 | 0.38 | 10
Maydown | NI | GU_501350 | Lisahally | Maydown |  |  |  |  | Oil | 100% |  |  | Waste wood | 12.74 | 17.6 |  | 40 | 17.6 |  |  |  |  | 9 |  |  |  |  | 0.067 | 24 | 0.04 | 0.04 | 4 | 0.5 | 2000 | 4000 | 6000 | 2 | 4